TABLE OF CONTENTS

SECTION 1. BASIC DATA AND REQUIREMENTS	3

SECTION 2. BASIC REQUIREMENTS FOR DESIGN    SOLUTIONS…………………………………….….7

SECTION 3. INITIAL DATA AND INFORMATION PROVIDED BY THE CUSTOMER ...………………10

SECTION 4. REQUIREMENTS FOR DESIGN DOCUMENTATION	12

SECTION 5. ADDITIONAL REQUIREMENTS AND DATA	15

SECTION 6. INTERFACES WITH ANPP SYSTEMS	16

SECTION 7. NORMS AND STANDARDS	17

LIST OF ABBREVIATIONS	19

TERMS AND DEFINITIONS	20

LIST OF APPENDICES	21

APPENDIX 1. LOCATION OF THE RAW RADIOACTIVE WASTE MANAGEMENT UNIT ON THE ANPP SITE	22

APPENDIX 2. MASS AND DIMENSIONAL CHARACTERISTICS OF RADIOACTIVE WASTE

CONTAINERS AND PACKAGES	24

APPENDIX 3. PRELIMINARY LAYOUT SCHEME AND GENERAL VIEWS OF THE RAW         RADIOACTIVE WASTE UNIT	26

APPENDIX 4. SSC RESPONSE SPECTRUM	33

APPENDIX 5. INSTALLATION CHARACTERISTICS OF THE SEGMENTED GAMMA       SCANNER……………………………………………………………………………………………….34

SECTION  1.	BASIC DATA AND REQUIREMENTS

| № п/п | List of Data and Requirements | Data and Requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
| 1.1. | Name of Object/Service | Radioactive Waste Characterization and Conditioning Unit (CCU) at the Armenian Nuclear Power Plant (ANPP). Development of the RW CCU Design Project |
| 1.2. | Location of the Facility | ANPP Industrial Site For the placement of the RW CCU on the ANPP industrial site, the Customer has designated a plot adjacent to Building No. 68, “Special Building,” as shown in Figure P1.1 (APPENDIX 1 to this TOR). |
| 1.3. | Basis for Design | “Program of Measures for the Management of RW Present at ANPP and Generated During the Extended Operation of ANPP Unit No. 2,” see clause 3.2 |
| 1.4. | Capacity (Throughput) of the RW CCU | The throughput of the RW CCU shall be at least 4 RW packages (metal containers with RW placed in reinforced concrete containers) ready for transfer to the Low- and Medium-Activity Radioactive Waste Storage (L/MA RW Storage) during a single 8-hour working shift. |
| 1.5. | Purpose of the RW CCU | The RW CCU is intended for performing radiological characterization of metal RW containers (standard 200-liter drums with solid RW, MK-0.2 containers, and tubular containers of various sizes containing salt melt from the deep evaporation facility), their placement into reinforced concrete protective containers (RC containers), with the possibility of filling the free space of the RC containers with cement grout, and for conditioning RW packages prior to their transfer to the Low- and Medium-Activity Radioactive Waste Storage (L/MA RW Storage). The RW CCU shall ensure: - reception and internal handling of RW containers within the unit; - buffer storage of at least 10 metal RW containers (characteristics provided in Tables P2.3, P2.4, and P2.5) pending radiological characterization; - radiological characterization of RW using a segmented gamma scanner (installation characteristics of the gamma scanner are provided in APPENDIX 5); - storage of at least 8 empty RC container sets (container, lid, and plugs) intended for loading with metal RW containers; (RC container characteristics are provided in Table P2.1) - handling of metal RW containers within an Intermediate Protective Container (IPC), IPC characteristics are provided in Table P2.2 - loading of metal RW containers, which have undergone radiological characterization, into RC containers; - preparation of cement grout for filling the free space of RC containers; - filling the free space in RC containers with cement grout - sealing and closure of the RC container lid; - accounting of conditioned RW; - temporary storage (curing) of at least 4 packages of conditioned RW for 24 hours to ensure initial setting of the cement grout prior to transfer to the L/MA RW Storage; - handover of the RW package at the boundary of the RW CCU for subsequent transfer to the L/MA RW Storage. |

| № п/п | List of Data and Requirements | Data and Requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
| 1.6. | Composition of the RW CCU | The RW CCU design shall include the following technologically interconnected and mutually complementary rooms, areas, structures, systems, components, and equipment: - Building and structures adjacent to the western wall of the “Special Building”; - The reception area for metal RW containers arriving from the Medium-Activity Waste Storage (MAW Storage), equipped with a fixed hydraulic lifting platform adjacent to the opening in the western wall of the superstructure above the “Special Building” roof at elevation +6.3 m; - The reception area for metal RW containers arriving from the RW Processing Complex (RWPC); - The buffer storage area for metal RW containers; - The RW container characterization area, equipped with a segmented gamma scanner - The storage area for empty RC containers (containers, lids, and plugs); - Cement grout preparation unit, comprising: - Cement storage silo [15], - Sand storage hopper for cement grout preparation [14], - Dosing hopper [12] - Equipment for feeding components into the Solution Mixing Unit (SMU), - SMU with a throughput of 0.5 m³ per batch [13], - Systems for weighing and dosing cement, sand, and water into the SMU; - A concrete pump with a hose for filling the free space of the RC container loaded with metal RW containers with cement grout; - The area for loading RC containers with metal RW containers after characterization, filling the free space of the container with cement grout, and transferring the RW package from the main RW CCU area to the curing area prior to transportation to the L/MA RW Storage; - The curing (holding) room for RW packages prior to transportation to the L/MA RW Storage; - The SMU room (Solution Mixing Unit room); - Lifting and handling equipment: - 5-ton overhead bridge crane with remote control; - A fixed hydraulic lifting platform with a lifting platform size of 2500 × 1500 mm and a load capacity of 3.5 tons (equipped with perimeter guardrails and two opening doors), intended for the transportation of personnel, the Intermediate Protective Container (IPC), and other loads between elevation +6.3 m (roof of the “Special Building”) and elevation ±0.0 m of the RW CCU; - A 15-ton forklift for handling RC containers and packages with conditioned RW, for transfer to the RW package curing room prior to transportation to the L/MA RW Storage, and for movement within areas outside the RW CCU building; |

1 Numbering is given in accordance with Figure П3.1

| № п/п | List of Data and Requirements | Data and Requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
|  |  | - Computerized workstation for personnel, equipped with RW accounting tools, RW CCU equipment control, and communication systems; - Intermediate Protective Container (IPC) to reduce personnel dose exposure during the transportation of metal RW containers; - Radiation monitoring and control system; - Closed-circuit television (CCTV) system for monitoring the movement of loads within the RW CCU, with video output to the computerized personnel workstation; - Fixed protective shields made of precast or monolithic concrete to protect personnel from ionizing radiation exposure; - Auxiliary systems (power supply, water supply, ventilation and air conditioning, computer network, communication) required for the normal operation of the RW CCU; - Fencing of the RW CCU area. The overall view and preliminary zoning and equipment layout of the RW CCU are shown in Figures P3.1 and P3.2; general views of the attached RW CCU layout are presented in Figures P3.3 – P3.6 (APPENDIX 3 to this TOR). The dimensions and configuration of the building, areas, and individual structures comprising the RW CCU shall be refined and adjusted by the Contractor, taking into account the technical requirements set out in Section 2 of this Terms of Reference (TOR) and the characteristics of the technological equipment proposed in the design. |
| 1.7. | Service Life | The service life of the RW CCU shall be at least 30 years. |
| 1.8. | Design Stages | The design is carried out in a single stage. The Contractor shall develop the main solutions for RW management technology, refine the requirements for equipment, construction materials, and structures, taking into account the technical requirements for the layout and functions of the RW CCU set out in Section 2 of this TR, and perform analysis and justification of the main technical and cost characteristics of the new construction facility. In parallel with the above, the following shall also be carried out: - Collection of all initial data required for the design of the facility, and coordination of the technical specifications (TS) for connecting the RW CCU to the ANPP external utility networks/communications; - Assessment of the impact of the RW CCU on existing ANPP buildings, structures, and utilities, both during construction and operation; Development of a project for the dismantling of the trestle structures (see Figure P3.7) between Building No. 68 “Special Building” and Building No. 68A “Special Building Expansion,” including temporary closure of the opening in the western wall of the superstructure above the “Special Building” roof, for the period until completion of the RW CCU construction; - Design of roads and utility networks/communications up to existing roads and connection points to the existing ANPP utility networks/communications specified by the Customer; - Development of the construction organization plan; - Development of working (detailed) documentation; |

| № п/п | List of Data and Requirements | Data and Requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
|  |  | - Preparation of the construction cost estimate in accordance with the legislation of the Republic of Armenia (RA); - Environmental impact assessment and preparation of the Environmental Impact Assessment (EIA) report; - Safety assessment and preparation of the Safety Analysis Report (SAR); - Development of Technical Specifications for all RW CCU equipment; - Development of the process flow diagram for the movement of RW containers, IPCs, and RW packages between the MAW Storage and the RW CCU, as well as within the RW CCU. Upon completion of the design, an independent review must be conducted by a licensed (authorized) organization, and following a positive conclusion, the design documentation shall be submitted for approval to the Republic of Armenia Committee on Nuclear Regulatory Safety. |

Section  2.	BASIC REQUIREMENTS FOR DESIGN SOLUTIONS

| № п/п | List of Data and Requirements | Data and Requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
| 2.1 | Requirements for the layout of the site provided by the Customer for the placement of the RW CCU | The layout solutions for the RW CCU shall be developed within the boundaries established by the Customer, as shown in Figure P1.1 (APPENDIX 1 to this TR). The layout solutions shall ensure an optimal zoning scheme and arrangement of main equipment, minimize operational costs, and provide optimal conditions for the work and movement of personnel, equipment, and flows of materials, RW containers, and packages within the RW CCU. |
| 2.2 | Technological Requirements for Buildings and Structures | The design shall provide for the following: - Reinforced concrete foundation (considering the expected loads in various areas/rooms) within the site provided by the Customer for the placement of the RW CCU; - Building equipped with roller shutters and a single-leaf door (on the south side) for personnel access and reception of RW containers; - Artificial lighting inside the premises and outside the building, within the RW CCU fenced area; - Windows on the north and south sides of the RW CCU building to provide combined artificial and natural lighting inside the RW CCU premises; - Electrically operated roller shutter gates on the south side of the RW CCU building for vehicle entry/exit delivering RW packages from the RW Processing Complex (RWPC), as well as a door for personnel access; - Open opening in the RW package dispatch area for the delivery of empty RC containers and the transfer of RW packages to the curing area prior to transportation to the L/MA RW Storage; - Electrically operated roller shutter gates on the north side of the RW package curing room prior to transportation to the L/MA RW Storage, for the transfer of empty RC containers and the dispatch of RW packages ready for transport to the L/MA RW Storage; - Door from the sand storage hopper area to the SMU room for access by personnel operating the SMU equipment; - Canopy over the sand storage hopper area and over the equipment intended for feeding sand into the dosing hopper located in the SMU room; - Supports for the installation of crane rails and an overhead bridge crane; - Roller conveyor installed on the fixed hydraulic platform, 1000 mm wide, with electric drive and adjustable travel speed, equipped with limit switches for automatic speed reduction and stopping of the pallet, with an IPC mounted on it upon reaching the end position; - Protective shields made of precast or monolithic reinforced concrete with a thickness of at least 400 mm; - Lightning protection for the RW CCU building; - Metal mesh fencing on a metal frame for the RW CCU area outside the building, with electrically operated sliding gates for the entry/exit of RC container sets and packages with conditioned RW (on the south side of the RW CCU). |
| 2.3 | Other technological | By risk level, the RW CCU building, structures, and constructions are classified as high-risk facilities – Category IV. |

| № п/п | List of Data and Requirements | Data and Requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
|  | Requirements | The systems and equipment of the RW CCU shall comply with Safety Class 3 requirements. The RW CCU building, structures, and constructions belong to Seismic Category 2. They shall be designed taking into account the response spectra of the Design Basis Earthquake (DBE) for PGA = 0.32 g, as shown in Figure P4.1 (APPENDIX 4 to this TR). The design shall provide for: - Maintaining the air temperature in the RW CCU building, including the SMU room and the RW package curing room prior to transportation to the L/MA RW Storage, within the range of +10°C to +25°C; - A collection system and settling tank for the collection and neutralization of SMU wastewater, with subsequent discharge into the ANPP sanitary sewer system - Collection and drainage of precipitation and meltwater from the RW CCU area into the industrial stormwater drainage system. |
| 2.4 | Requirements for Structural and Spatial-Planning Solutions of the Building, Structures, Systems, and Equipment | The structural and spatial-planning solutions for the building, structures, and systems shall comply with the requirements of the regulatory and technical documentation (see Section 7) and the technical requirements specified in this section. - RW CCU Building - The load-bearing structures of the building shall be made of steel with a protective anticorrosion coating. - For the external walls and roofing, insulated wall panels clad with profiled metal having an anticorrosion coating shall be used; these panels shall be fixed to a framework mounted on the load-bearing steel structures. - the building roof shall be of a single-slope type, with variable height over individual sections of the building. - the roof height above the main UHK RW facility area, as well as above the RSU room and the RW package holding area, shall be determined taking into account the technological features of the processes and equipment involved in handling RW packages. - provide reinforced concrete walls² with a thickness of at least 200 mm between the main UHK RW facility area, the RSU room, and the RW package holding area. - Opening in the western wall of the superstructure above the “Special Building” roof between the “Special Building” roof and the main RW CCU area at elevation +6.3 - The wall opening, in the section not covered by the roller conveyor system for transporting RW containers on the roof of the “Special Building” (this system is not within the scope of this TOR), which connects to the roller conveyor installed on the fixed hydraulic lifting platform, shall be equipped with a 1000 mm high guard fence with a gate for personnel movement to/from the fixed hydraulic platform. The gate shall be fitted with an interlock (electromagnetic lock with limit switch) that prevents opening when the platform starts moving down from elevation +6.3. |

2 Толщина бетонных стен должна быть уточнена в процессе проектирования по результатам оценки безопасности

| № п/п | List of Data and Requirements | Data and Requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
|  |  |  The wall opening in the section covered by the roller conveyor shall be equipped with a protective fence at least 1000 mm high, with a gate that is closed by the operator and automatically locked (electromagnetic lock with limit switch) when the platform moves down from elevation +6.3, and automatically unlocked for opening after the platform is raised back to elevation +6.3. The movement of the platform is blocked if the gate is not closed.. - Lifting Equipment Overhead Bridge Crane:: - The crane’s operating range shall cover the entire area of the main RW CCU facility, providing full coverage of the main area as shown in Figure P3.2 (APPENDIX 3 to this TR); - The crane shall be equipped with a camera for visual monitoring of cargo handling operations (CCTV) between different zones within the RW CCU, with the video feed displayed at the computerized personnel workstation. Fixed Hydraulic Platform: - The platform’s deck shall be equipped with a protective railing at least 1000 mm high; - The railing shall be equipped with hinged gates for personnel entry/exit and IPC transfer on the side adjacent to the “Special Building” and on the lateral side (towards the characterization area) to allow personnel access and IPC handling without the need to lift the container over the railing. - Canopy over the Sand Storage Hopper Area - The canopy over the sand storage hopper area shall be a continuation of the SMU room roof and made of the same roofing material. - Fixed Protective Shields³ made of precast or monolithic concrete - The fixed protective shields shall be made of precast or monolithic concrete with a thickness of at least 400 mm, as shown in Figure P3.2 (APPENDIX 3 to this TR). - In the RW container buffer storage area, on three sides, - In the RW container characterization area, on three sides, with an opening (along the long side of the protective shield) spanning the full height of the shield and at least 1100 mm wide, to allow IPC entry into the characterization area without the need to lift the container over the protective shield, - Along the area for loading RCs with RW containers and for issuing packages of conditioned RW; - Approximate height of the protective shields: - In the RW container buffer storage area – 1300 mm, |

3 Толщина и высота защитных экранов из бетона должны быть уточнены в процессе проектирования по результатам оценки безопасности

| № п/п | List of Data and Requirements | Data and Requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
|  |  | - In the RW container characterization area – 2000 mm,, - Along the area for loading RCs with RW containers and for issuing packages of conditioned RW – 1500 mm. |
| 2.5 | Power Supply | The design shall provide power supply for all systems and equipment of the RW CCU from a single power distribution panel, which shall be located within the RW CCU building. |
| 2.6 | Lighting | The design shall provide: - Artificial and combined lighting for the RW CCU rooms and the sand storage hopper area; - Outdoor lighting around the perimeter of the RW CCU. The lighting shall be designed using energy-saving technologies. |
| 2.7 | Other Requirements | Intra-facility communications are included in the scope of the RW CCU design. The design shall provide emergency power supply for the automatic fire detection systems and the radiation monitoring and control systems. |
| 2.8 | Communication System | The design shall provide a communication system compatible with the existing communication equipment at the Armenian NPP, as well as a local (on-site) radio communication system. |
| 2.9 | Closed-Circuit Television (CCTV) System | The design shall provide a system for monitoring cargo movement within the RW CCU, with the video feed displayed at the computerized personnel workstation. |
| 2.10 | Fire Alarm and Fire-Fighting Equipment | The design shall equip the RW CCU with fire alarm and fire-fighting systems in accordance with the current fire safety regulations of the Republic of Armenia (see Section 7). |
| 2.11 | Site Development, Access Roads, and Driveways | Access roads and driveways: - The roads and driveways shall be designed from the boundary of the RW CCU concrete foundation to the existing asphalt-paved roads on the Armenian NPP site; The design shall provide asphalt-paved roads capable of supporting loads at least equal to those arising during the transportation of RW packages, taking into account the weight and dimensions of the vehicles and the transported cargo. Fencing: - The design shall provide a fence around the perimeter of the area outside the RW CCU building; - The fence shall be equipped with automatic sliding gates with electric drive |

SECTION 3.	BASIC INPUT DATA AND INFORMATION PROVIDED BY THE CUSTOMER

| № п/п | List of Data and Requirements | Data and Requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
| 3.1 | Technical Data Provided by the Customer | Upon the Contractor’s request, the Customer shall indicate the connection points of the RW CCU to the existing Armenian NPP utility networks/communications (electrical networks, taking into account the consumer category, communication lines, computer network, etc.). |
| 3.2 | Number of RW Packages Delivered to the Facility | Up to 1,500 metal containers with low- and intermediate-level RW per year. The mass and dimensional characteristics of RW containers are provided in APPENDIX 2 to this TR. |
| 3.3 | Other Basic Data | Any additional data available at the Armenian NPP that may be required for the design of the RW CCU—for example, detailed information on waste characteristics, the radiation situation within the area allocated for the RW CCU, the site plan, and other data not included in this TOR—may be provided to the Contractor upon separate request. The Contractor is responsible for verifying and, if necessary, clarifying the received data and information. |

SECTION 4.	REQUIREMENTS FOR DESIGN DOCUMENTATION

| № п/п | List of Data and Requirements | Data and Requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
| 4.1 | Basic Requirements for the Development of Design Documentation | The documentation shall be developed in accordance with the requirements established in the Republic of Armenia regarding the composition of design documentation sections and their content requirements. Composition of the design documentation: Section 1.1. Explanatory Note. Section 1.2. Preliminary Design (sketches) for obtaining the architectural design assignment. Section 1.3. Bill of Quantities. Section 2. Site Layout Plan. Section 3. Architectural Solutions. Section 4. Structural and Spatial-Planning Solutions. Section 5. Information on engineering equipment, utility networks, list of engineering-technical measures, and content of technological solutions. Section 6. Construction Organization Plan. Section 7. List of Environmental Protection Measures. Section 8. Radiation Safety Measures. Section 9. Fire Safety Measures. Section 10.1. Measures to Ensure Compliance with Energy Efficiency Requirements and the Requirements for Equipping Buildings, Structures, and Facilities, Including Installation of Meters for Consumed Energy Resources. Section 10.2. Requirements for Ensuring the Safe Operation of Capital Construction Facilities. Section 11.1. Construction Cost Estimate for Capital Construction Facilities. Section 11.2. Consolidated Construction Cost Estimate for the Facility. Section 12. Other Documentation. |
| 4.2 | Safety Assessment and Development of the Safety Analysis Report (SAR) | The Contractor is responsible for performing the safety assessment and developing the Safety Analysis Report (SAR) for the RW CCU. The Safety Analysis Report (SAR) for the RW CCU shall include: Introduction with a brief description of the objectives of the SAR Methodology for Conducting the Safety Assessment Safety Assessment Context - Objectives of the Safety Assessment - Applied Approach - Regulatory Basis - Safety Assessment Criteria - Timeframe of the Safety Assessment Description of the RW CCU, Its Activities, and the Waste •Description of the Site • Description of the RW CCU • Radiation Monitoring and Radiation Situation in and around the RW CCU • Key Characteristics of RW Containers • Description of RW Handling Activities • Maintenance and Repair • Technical Inspection and Control |

| № п/п | List of Data and Requirements | Data and Requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
|  |  | • Personnel Dose Monitoring System at the ANPP during RW Handling • Development and Justification of Scenarios • Identification and Screening of Hazards • Definition of the Normal Operation Scenario • Definition of Potential Operational Deviations and Accident Scenarios • Description of the Scenarios Models Used in the Safety Assessment Execution of Calculations, Evaluations, and Analysis of Results • Assessment of the Maximum Individual Radiation Dose under the Normal Operation Scenario • Personnel Dose Loads under Potential Operational Deviations and Accident Conditions • Analysis of Uncertainties and Sensitivity of Results to Changes in Calculation Parameter Values Conclusions and Recommendations |
| 4.3 | Environmental Impact Assessment (EIA) | The Contractor is responsible for developing the Environmental Impact Assessment (EIA) for the RW CCU. The Environmental Impact Assessment (EIA) for the RW CCU shall include: Introduction with a brief description of the objectives of the eia Description of the activity and its objectives Description of alternative activity options Assessment of Potential Economic and Environmental Damage, Including Forms and Timing of Compensation Assessment of Individual Environmental Components, Natural Resources, and Potential Changes in Conditions and Their Magnitude in Case the Activity Is Implemented Potential Social Impact Potential Impact on Human Health Assessment of the Risks from Potential Emergency Situations Impact on the Climate Justification of the Activity’s Compliance with Approved Fundamental Documents Justification of the Selected Option Environmental Management Plan Monitoring Program for the Impact of the Planned Activity Summary Materials (maps, diagrams, charts, tables indicating sources of initial data) Information on Obstacles Encountered During the Assessment and Report Preparation Potential Environmental Impact During the Construction, Operation, and Decommissioning Phases |
| 4.4 | Technical Specifications | The Contractor is responsible for developing technical specifications for all systems and equipment required for the operation of the RW CCU, except for the segment gamma scanner model G3251-340 already available at the Armenian NPP. |

| № п/п | List of Data and Requirements | Data and Requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
|  |  | The list of technical specifications to be developed shall be agreed upon with the Customer. |
| 4.5 | Requirements for Cost/Estimate Documentation | The cost/estimate documentation shall be prepared in accordance with the current regulations of the Republic of Armenia (see Section 7). |
| 4.6 | Guidelines for the Preparation of Additional Documentation as Part of the Project (Demonstration Materials, Their Scope, and Format) | Demonstration materials for public presentation (in print — brochures, and in electronic format) shall be developed by the Contractor. The scope and types of demonstration materials shall be agreed upon separately with the Customer. |
| 4.7 | Number of Copies of the Design Documentation | The design documentation shall be submitted in 4 (four) complete hard copies and 1 (one) electronic copy in PDF format. The cost estimate documentation shall be submitted in 1 (one) hard copy and 1 (one) electronic copy in Excel format. Any additional formats shall be agreed upon at the initial stage of design. |
| 4.8 | Approval of Design Documentation | The design documentation shall be submitted by the Contractor for approval in the Armenian language. The Contractor shall provide the documentation and support it during the review by governmental authorities or licensed and/or authorized organizations, and, together with the Customer, shall address any comments until a positive conclusion is obtained. The payment of fees for the review conducted by the governmental authorities of Armenia shall be made by the Armenian NPP. |
| 4.9 | Other Requirements | The project must comply with the regulatory documentation in effect at the time of the contract signing (see Section 7). Subsequent changes may be made by an additional agreement between the parties. |

SECTION 5.	ADDITIONAL REQUIREMENTS AND DATA

| № п/п | List of Data and Requirements | Data and Requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
| 5.2 | Operating Mode of the Main Equipment of the CCU for RW | 8 hours per day, 250 days per year |
| 5.3 | Personnel Working Schedule | The personnel work schedule is one shift, 8 hours per day. |
| 5.8 | Work Execution Schedule | The timeframe for work execution is 9 months from the date of conclusion of the contract for the design of the CCU for RW. In the event of delays in contract performance, no later than 3 months before the expiration of the established data, the Contractor shall submit to the Customer a request for extension of the work execution period, with justification of the duration required for the full completion of the works. The Contractor’s financial responsibility for delays shall be governed by the provisions of the contract. |
| 5.9 | Making Amendments and Additions | The Terms of Reference (TOR) may be clarified and supplemented by mutual agreement of the parties no later than 30 calendar days prior to the deadline for the preparation of the design documentation under the contract. |
| 5.10 | Norms and Standards | Section 7 contains a list of the general norms and standards applicable to RW management facilities. If the application of additional requirements is necessary during the preparation of the design documentation for the CCU for RW, the Contractor shall prepare and agree with the ANPP a list of specific standards that the design solutions must comply with. |
| 5.10 | Subcontractors | When engaging subcontractors, the Contractor assumes full responsibility for the execution and quality of the works assigned to the subcontractors. |
| 5.11 | Design (Author’s)Supervision | The Contractor shall carry out Design Supervision for all construction, installation, and commissioning activities, including works performed by subcontractor(s), in accordance with a separate agreement with the ANPP, to be executed at the facility’s construction stage. |

SECTION 6.	Interfaces with ANPP Systems

| № п/п | List of Data and Requirements | Data and Requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
| 6.1 | Interfaces4 with ANPP Systems | The equipment of the CCU for RW shall have interfaces with the following ANPP systems: Power Supply – connection to the 0.4 kV CRU Radiation Monitoring and Control System – transmission of information to the RSB panel Fire Water Supply – connection to the fire network of the “Special Building” Fire Alarm System – transmission of signals to the MCC Communication System – connection to the plant ATS Computer Network – connection to one of the network hubs Stormwater Drainage System – connection to the industrial stormwater sewer MSU Wastewater Collection and Disposal System – connection to the domestic sewer |

4 The Contractor may suggest other interfaces with ANPP systems that are not included in this table.

Section 7.	Norms and Standards

| № | Name |
| --- | --- |
| International Standards / Documents / Recommendations |  |
| 1. | IAEA SF-1, Fundamental Safety Principles |
| 2. | IAEA GSR Part 3, Radiation Protection and Safety of Radiation Sources: International Basic Safety Standards |
| 3 | IAEA Safety Standards Series No. GSR Part 4, Safety Assessment for Facilities and Activities |
| 4. | IAEA No. GSR Part 5, Predisposal Management of Radioactive Waste |
| 5. | IAEA TS-R-1, Regulations for the Safe Transport of Radioactive Material |
| 6. | IAEA GSG-1, Classification of Radioactive Waste |
| 7. | IAEA GSG-3, The Safety Case and Safety Assessment for the Predisposal Management of Radioactive Waste |
| 8. | IAEA TECDOC-1817, Selection of Technical Solutions for the Management of Radioactive Waste |
| 9. | IAEA GSR Part 6 Decommissioning of Facilities |
| 10. | Council Directive 2013/59/Euratom of 5 December 2013 laying down basic safety standards for protection against the dangers arising from exposure to ionizing radiation, and repealing Directives 89/618/Euratom, 90/641/Euratom, 96/29/Euratom, 97/43/Euratom and 2003/122/Euratom |
| 11. | WENRA Report: Waste and Spent Fuel Storage Safety Reference Levels, 2014 |
| National Standards / Documents / Recommendations |  |
| 1. | Law of the Republic of Armenia on the Safe Use of Atomic Energy for Peaceful Purposes, NO-295 dated 01.02.1999 ՀՀ օրենքը խաղաղ նպատակներով ատոմային էներգիայի անվտանգ օգտագործման մասին ՀՕ- 285 01.02.99թ. (Закон РА о безопасном использовании атомной энергии в мирных целях НО-295 от 01.02.99 г.) |
| 2. | Law of the Republic of Armenia on Licensing, NO-193 dated 30.05.2001 ՀՀ օրենքը Լիցենզավորման մասին ՀՕ-193 30.05.01թ. (Закон РА о лицензировании НО-193 от 30.05.01 г.) |
| 3. | Law of the Republic of Armenia on Environmental Impact Assessment and Expertise, NO-110-N with amendments dated 03.05.2023 ՀՀ օրենքը Շրջակա միջավայրի վրա ազդեցության գնահատման և փորձաքննության մասին ՀՕ- 110-Ն 21.06.14թ. (Закон РА об оценке воздействия на окружающую среду и экспертизе НО-110-N с изменениями от 03.05.23 г.) |
| 4. | Law of the Republic of Armenia on Fire Safety, NO-176 dated 15.05.2001 ՀՀ օրենքը Հրդեհային անվտանգության մասին ՀՕ-176 15.05.01թ. (Закон РА о пожарной безопасности НО-176 от 15.05.01) |
| 5. | Government Decree of the Republic of Armenia “On Approval of Radiation Safety Standards,” 1219-N dated 18.09.2006 ՀՀ կառավարության որոշում «Ճառագայթային անվտանգության նորմերը հաստատելու մասին» 1219-Ն 18.09.06թ. (Постановление Правительства РА «Об утверждении норм радиационной безопасности» 1219-Н от 18.09.06 г.) |
| 6. | Government Decree of the Republic of Armenia “On Approval of Radiation Safety Rules,” 1489-N dated 18.09.2006 ՀՀ կառավարության որոշում «Ճառագայթային անվտանգության կանոնները հաստատելու մասին» 1489-Ն 18.09.06թ. (Постановление Правительства Республики Армения «Об утверждении Правил радиационной безопасности» 1489-Н от 18.09.06 г.) |
| 7. | Government Decree of the Republic of Armenia “On Approval of the Procedure for Handling Radioactive Waste,” 631-N dated 04.06.2009 ՀՀ կառավարության որոշում «Ռադիոակտիվ թափոնների կառավարման կարգը հաստատելու մասին» 631-Ն 04.06.09թ. (Постановление Правительства РА «Об утверждении Порядка обращения с радиоактивными отходами» 631-Н от 04.06.09 г.) |

| № | Наименование |
| --- | --- |
| 8. | Government Decree of the Republic of Armenia “On Approval of the Procedure for Licensing and the License Form for the Design of Devices, Equipment, and Systems Important for the Safety of Nuclear Energy Facilities,” 257-N dated 10.02.2005 ՀՀ կառավարության որոշում «Ատոմային էներգիայի օգտագործման օբյեկտների համար անվտանգության տեսակետից կարևոր սարքերի, սարքավորումների, համակարգերի նախագծման լիցենզավորման կարգը և լիցենզիայի ձևը հաստատելու մասին» 257-Ն10.02.05թ (Постановление Правительства Республики Армения «Об утверждении порядка лицензирования и формы лицензии на проектирование устройств, оборудования, систем, важных с точки зрения безопасности для объектов использования атомной энергии» 257-Н10.02.05 г.) |
| 9. | Procedure for Issuing Permits and Other Documents for the Execution of Construction Works in the Republic of Armenia, Government Decree 596-N dated 19.03.2015 Հայաստանի Հանրապետությունում կառուցապատման նպատակով թույլտվությունների եվ այլ փաստաթղթերի տրամադրման կարգ ՀՀ կառավարության որոշում 596-Ն 19.03.15 թ. Порядок выдачи разрешения и иных документов с целью производства строительных работ в РА. Постановление Правительства Республики Армения 596-Н 19.03.15 г. |
| 10. | Order of the Chairman of the Committee on Urban Development of the Republic of Armenia “On Approval of a Number of Normative and Technical Documents Subject to Localization and Effective in the Territory of the Republic of Armenia, and on Annulment of the Order of the Minister of Urban Development of the Republic of Armenia No. 82 dated 01 October 2001,” No. 11-N dated 14.06.2022 ՀՀ քաղաքաշինության կոմիտեի նախագահի հրաման «Հայաստանի Հանրապետության տարածքում գործող` տեղայնացման ենթակա մի շարք նորմատիվատեխնիկական փաստաթղթեր հաստատելու եվ հայաստանի հանրապետության քաղաքաշինության նախարարի 2001 թվականի հոկտեմբերի 1-ի հ 82 հրամանն ուժը կորցրած ճանաչելու մասին» 11- Ն 14.06.22 թ. (Приказ Председателя Комитета по градостроительству РА «Об утверждении ряда нормативно-технических документов, подлежащих локализации и действующих на территории Республики Армения, и признании утратившим силу приказа Министра градостроительства Республики Армения от 1 октября 2001 года № 82» № 11-Н от 14.06.22) |
| 11. | СНРА 13-02-2022 “Occupational Safety in Construction” ՀՀՇՆ 13-02-2022 «Անվտանգության տեխնիկա շինարարությունում» (СНРА 13-02-2022 «Техника безопасности в строительстве») |
| 12. | СНРА 20-05-2022 “Protection of Building Structures Against Corrosion” ՀՀՇՆ 20-05-2022 «Շինարարական կոնստրուկցիաների պաշտպանությունը կոռոզիայից» (СНРА 20-05-2022 «Защита строительных конструкций от коррозии») |
| 13. | СНРА 31-04-2022 “Roofs and Roofing Works” ՀՀՇՆ 31-04-2022 «Տանիքներ և տանիքածածկեր» (СНРА 31-04-2022 «Кровли и кровельные работы») |
| 14. | СНРА 32-01-2022 Roads / Roadways ՀՀՇՆ 32-01-2022 «Ավտոմոբիլային ճանապարհներ» / СНРА 32-01-2022 «Автомобильные дороги» |
| 15. | СНРА IV-10.01.01-2006 “Foundations of Buildings and Structures” ՀՀՇՆ IV-10.01.01-2006 «Շենքերի և կառուցվածքների հիմնատակեր» (СНРА IV-10.01.01-2006 «Основания зданий и сооружений») |
| 16. | СНРА 13-03-2022 Load-Bearing and Enclosing Structures ՀՀՇՆ 13-03-2022 «Կրող և պատող կոնստրուկցիաներ» (СНРА 13-03-2022 «Несущие и ограждающие конструкции») |
| 17. | GOST 27751-2014 “Reliability of Building Structures and Foundations. General Provisions” ԳՕՍՏ 27751-2014 Շինարարական կառույցների և հիմնատակերի հուսալիություն. Հիմնական դրույթներ (ГОСТ 27751-2014 «Надежность строительных конструкций и оснований. Основные положения») |
| 18. | СНРА 52-01-2 “Concrete and Reinforced Concrete Structures” ՀՀՇՆ 52-01-2 Բետոնե և երկաթբետոնե կոնստրուկցիաներ (СНРА 52-01-2 «Бетонные и железобетонные конструкции») |
| 19. | СНРА 20.04 “Design Standards for Seismic-Resistant Structures” ՀՀՇՆ 20.04- Երկրաշարժադիմացկուն շինարարություն նախագծման նորմեր (СНРА 20.04 «Нормы проектирования сейсмостойких конструкций») |
| 20. | СНРА “Organization of Construction Activities” ՀՀՇՆ «Շինարարական արտադրության կազմակերպում» շինարարական նորմեր (СНРА «Организация строительного производства») |

List of Abbreviations

| № п/п | Abbreviation | Abbreviation Expansion |
| --- | --- | --- |
| 1 | ANPP | Armenian Nuclear Power Plant |
| 2 | ATS | Automatic Telephone Station |
| 3 | ГОСТ/GOST | State Standard |
| 4 | RCC | Reinforced Concrete Container |
| 5 | SSE | Safe Shutdown Earthquake / Seismic Safety Earthquake |
| 6 | RSC | Radiation Safety Control |
| 7 | CRU | Comprehensive Switchgear Unit |
| 8 | RA CNRS | Republic of Armenia Committee on Nuclear Regulatory Safety |
| 9 | SAR | Safety Analysis Report |
| 10 | EIA | Environmental Impact Assessment |
| 11 | DD | Design Documentation. |
| 12 | IPC | Intermediate Protective Container. |
| 13 | DPS | Design and Estimate Documentation. |
| 14 | RA | Republic of Armenia. |
| 15 | RW | Radioactive Waste. |
| 16 | MSU | Solution Mixing Unit. |
| 17 | MAW | Medium-Activity Waste. |
| 18 | ACN | Armenian Construction Norms. |
| 19 | TOR | Terms of Reference. |
| 20 | ТS | Technical Specifications. |
| 21 | CCU | Characterization and Conditioning Unit. |
| 22 | L/MA RW Storage | Low- and Medium-Activity Radioactive Waste Storage. |
| 23 | MAW Storage | Medium-Activity Waste Storage. |
| 24 | MCC | – Main Control Board. |

Terms and Definitions

| № п/п | Terms | Definitions |
| --- | --- | --- |
| 1 | Radioactive Waste Conditioning | Conversion of radioactive waste into a form suitable for transportation, storage, and disposal. |
| 2 | Container (for Radioactive Waste) | A container is a vessel intended for the placement and secure retention of the waste form for the purposes of subsequent handling, transportation, storage, and/or disposal; it is a component of the radioactive waste packaging and also serves as an external barrier protecting the waste form from external influences. |
| 3 | Metal Container | Metal containers of cylindrical shape of various types and sizes, including 200-liter |
| 4 | Waste Packaging | The final product of radioactive waste conditioning, which includes the waste form and any containers and internal barriers (e.g., absorbent materials and liners), prepared in accordance with the requirements for handling, transportation, storage, and/or disposal. |
| 5 | Radioactive Waste Packaging (RW Packaging) | Container with radioactive waste |
| 6 | Waste Characterization | Determination of the physical, chemical, and radiological properties of waste in order to assess the need for further treatment, processing, or conditioning, or to evaluate its suitability for subsequent handling, processing, storage, or disposal |

List of Appendices

| Appendix Number | Title of the Appendix | Page Number |
| --- | --- | --- |
| 1 | Location of the CCU for RW on the ANPP Site | 22 |
| 2 | Mass and Dimensional Characteristics of Radioactive Waste Containers and Packaging | 24 |
| 3 | Preliminary Layout Diagram and General Views of the CCU for RW | 26 |
| 4 | Response Spectrum of the SSE | 33 |
| 5 | Installation Characteristics of the Segmented Gamma Scanner | 34 |

Appendix 1.

Location of the CCU for RW on the ANPP Industrial Site

Figure P1.1 – Site Area for the Characterization and Conditioning Unit for Radioactive Waste

Appendix 2

Mass and Size Specifications of RW Containers and Packaging

Table P2.1 – Mass and Dimensional Characteristics of Empty and Filled Reinforced Concrete Containers

| Parameter | Value |
| --- | --- |
| Mass of RW Packaging, kg | up to 12000 |
| Mass of the Container Set (Body and Lid), kg | up to 4400 |
| External Dimensions¹, mm |  |
| length | 1700 |
| width | 1700 |
| height | 1350 |

Table P2.2 – Mass and Dimensional Characteristics of Empty and Filled Intermediate Protective Containers (IPC)

| Parameter | Value |
| --- | --- |
| Mass of RW Packaging, kg | up to 3300 |
| Mass of the Container Set (Body and Lid), kg | up to2600 |
| External Dimensions², mm |  |
| diameter | 920 |
| height | 1450 |

Table P2.3 – Characteristics of Metal Piped Containers with Salt Melt

| Parameter | Value |  |  |  |
| --- | --- | --- | --- | --- |
|  | Type1 | Type 2 | Type 3 | Type 4 |
| Mass of RW Packaging, kg | up to 350 | up to 480 | up to 650 | up to 550 |
| Net Mass of the Container, kg | 105 | 100 | 120 | 75 |
| External Dimensions, mm |  |  |  |  |
| diameter | 426 | 530 | 630 | 630 |
| height | 953 | 953 | 959 | 953 |

Table P2.4 – Mass and Dimensional Characteristics of the MC-0.2 Metal Container with Salt Melt

| Parameter | Value |
| --- | --- |
| Mass of RW Packaging, kg | up to480 |
| Net Mass of the Container, kg | 78 |
| External Dimensions, mm |  |
| diameter | 560 |
| height | 910 |

1 The dimensions of the RC containers will be refined/confirmed by the Customer at the design stage.

2 The dimensions of the IPC will be refined/confirmed by the Customer at the design stage.

Table P2.5 – Characteristics of 200 L Drums with Solid RW

| Parameter | Value |
| --- | --- |
| Mass of RW Packaging, kg | up to 30 |
| Net Mass of the Container, kg | up to450 |
| External Dimensions, mm |  |
| diameter | up to 603 |
| высота | up to 848 |

Appendix 3.

Preliminary Layout Diagram and General Views of the CCU for RW

Figure P3.1 – General View of the CCU for RW Placement

Figure P3.2 – Preliminary Layout Diagram and Placement of CCU for RW Equipment

Legend of Symbols:

| 1. Receiving area for RW containers from MAW Storage | 2. Receiving area for RW containers from RW Processing Facility |
| --- | --- |
| 3. Buffer storage area for metal RW containers | 4. Area for Characterization of RW Containers |
| 5. Storage area for empty RC containers (bodies, lids, plugs) | 6. Intermediate Protective Container (IPC) |
| 7. Area for Loading RC Containers with Radioactive Waste, Subsequent Cementation, and Issuance of Conditioned RW Packaging | 8. Overhead Crane |
| 9. Hydraulic lifting platform | 10. Room for Curing RW Packages Prior to Transportation to L/MA RW Storage |
| 11. MSU Room (MSU = Solution Mixing Unit) | 12. Bunker-Feeder |
| 13. Solution Mixing Unit | 14. Sand storage bunker |
| 15. Cement Storage Silo | 16. Fencing of the CCU for RW Placement Area |
| 17. Forklift | 18. Computerized Workstation |

Flowchart

of Material Streams and Main Technological Operations in the RW Management Process at the CCU for RW

(according to the preliminary layout diagram shown in Figure P3.2)

Figure P3.3 – General View of the CCU for RW Building and Site

Figure P3.4 – General View of the Preliminary Spatial and Layout Solutions of the CCU for RW

Figure P3.5 – General Views of the Main Room of the CCU for RW

Figure P3.6 – General Views of the RW Package Curing Room Prior to Transportation to L/MA RW Storage

Figure P3.7 – General View of the Connecting Overpass Between the Special Building and Its Extension, Subject to Dismantling

Appenndix 4.

SSE Response Spectra

Figure P4.1

Appendix 5.

INSTALLATION CHARACTERISTICS OF THE SEGMENTED GAMMA SCANNER, MODEL G3251-340

| Wide-range segmented gamma scanner |  |
| --- | --- |
| Weight: | 1250 кг (прибл.) |
| Dimensions (L × W × H): | 3,12 m х 2,22 m х 2,69 m |