| “HAYAKAKAN ATOMAYIN ELECTRAKAYAN” CLOSED JOINT-STOCK COMPANY (ARMENIAN NUCLEAR POWER PLANT) AGREED BY APROVED BY ANPP DIRECTOR HAEK CJSC DIRECTOR GENERAL _______________ M.Vardanyan _____________ E.Martirosyan _____________________ 2026 ___ 2026 TERMS OF REFERENCE for the Design of a Storage Facility for Low-Level and Intermediate-Level Radioactive Waste at the Armenian NPP ENDORSED BY AGREED BY DCE on safety ANPP Chief Engineer ______________ V. Atoyan ______________A. Grigoryan _____ ______________2026 _____ ______________2026 METSAMOR-2026 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Position | Name/Surname | Signature | Date |  |
| Reviewed by | Head of RAWDD | H. Hobosyan |  |  |  |
| Developed by | DH of RAWDD | N. Avakyan |  |  |  |

CONTENT

SECTION 1.	basic data and requirements 	 3

SECTION 2.	basic requirements for design solutions	 4

SECTION 3.	INITIAL DATA AND INFORMATION PROVIDED BY THE CUSTOMER	 8

SEcTION 4.	Requirements to design documentation	 8

SECTION 5.	 ADDITIONAL REQUIREMENTS AND DATA	 9

SECTION 6.	INTERFACES WITH THE SYSTEMS OF THE ANPP 	 10

SECTION 7.	NORMS AND STANDARDS 	 11

LIST OF APPENDICES	13

# SECTION 1.  basic data and requirements

| № | List of data and requirements | Data and requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
| 1.1 | Facility/Service | Low- and intermediate-level radioactive waste storage facility (LILRW SF) at the Armenian Nuclear Power Plant. Design development. |
| 1.2. | Location of the facility | The ANPP industrial site The Customer has identified two sites for LILRW SF, as shown in Fig. P1.1 (APPENDIX 1 to this TOR). |
| 1.3. | Basis for design | “Program of measures of radioactive waste management available at the ANPP and generated during the additional operating period of ANPP Unit 2”, see paragraph 3.2 |
| 1.4. | Capacity of LIL RW storage facility | The design should provide for the creation of radioactive waste package storage facilities in two sets. Each set should include two adjacent storage modules with a capacity of 11521 radioactive waste packages (reinforced concrete containers (RCC)) each. The total storage capacity is 4,608 radioactive waste packages. |
| 1.5. | Purpose of LIL RW storage facility | The LIL RW storage facility should ensure: - receiving, processing, and placing radioactive waste packages for storage; - accounting for and tracking packages placed in storage; - retrieval of any individual radioactive waste package and inspection, followed by re-placement in its original storage location or in a designated backup location. |
| 1.6. | Composition of LIL RW storage facility | The LIL RW storage facility should consist of 4 storage modules each containing 1152 radwaste packages. For each set of the LIL RW storage facility, the design must include the following technologically interconnected and complementary components, systems, and equipment: 1) a reception area (RA) used for the reception, incoming inspection, inspection, and accounting of radwaste packages (shared between the two compartments); 2) two storage compartments (SC) for radwaste packages; 3) lifting equipment (a cross-bar overhead crane) with visual monitoring of the operations for moving reinforced concrete elements into the LIL RW storage facility (industrial television); 4) Radiation monitoring and control system; 5) Checkpoint for personnel of LIL RW storage facility; 6) Sanitary checkpoint for personnel of LIL RW storage facility; 7) Secondary radioactive waste collection area; 8) Decontamination area; 9)Auxiliary systems (power supply, air conditioning, internet, communications, etc.) supporting the operation of LIL RW storage facility. The dimensions and configuration of the structures and constructions that make up the LIL RW storage facility are determined taking into account the technical requirements set out in Section 2 of this Terms of Reference (ToR) and the operational features of the technological equipment. |
| 1.7. | Service life | The service life of LIL RW storage facility should be at least 50 years. |
| 1.8. | Design stages | The design is completed in a single stage. The contractor will develop key technology solutions, determine the need for equipment, building materials, and structures, evaluate the technical requirements for the layout and functions of the LIL RW storage facility, as outlined in Section 2 of this ToR, and analyze and justify the key technical and cost characteristics of the construction of the new facility. In parallel with the above, the following activities are performed: - collection of all initial data required for the design of the facility and approval of the technical specifications for connecting the LIL RW storage facility to the external utility networks/communications of the ANPP; - assessment of the impact of the LIL RW on existing buildings, structures and communications of the ANPP, as well as on the safe operation of the ANPP, both during construction and during operation; - development of design solutions for dismantling the structures of the old outdoor switchyard and preparing the construction site; - designing of roads and utility networks/communications to existing roads and connection points to existing utility networks/communications of the ANPP, specified by the Customer; - development of a construction management plan; - calculations and development of design documentation; - development of a construction estimate in accordance with the requirements of the legislation of the Republic of Armenia (RA); - environmental impact assessment and development of an environmental impact report (EIR); - safety assessment and development of a safety analysis report (SAR) - development of Technical Specifications for all the equipment of the LIL RW storage facility, - development of a flow diagram of the movement of reinforced concrete structures with radioactive waste from the radwaste characterization and conditioning unit to the LIL RW storage facility, as well as within the LIL RW storage facility. Upon completion of the design, an independent examination by a licensed (authorized) organization is required, and after receiving a positive conclusion, the ANPP will submit the design documentation for approval to the RA Committee for Nuclear Safety Regulation (RA NSR Committee). |
| 1.9. | Other requirements | In terms of risk level, the structures and components of LIL RW storage facility are classified as high-risk facilities – Category IV [9]. The systems and equipment of the LIL RW storage facility must comply with the requirements of Safety Class 3. The structures and components of the LIL RW storage facility belong to Category 2 of seismic resistance. They must be designed taking into account the Response Spectra of the Review Level Earthquake (RLE) for PGA=0.32g, which is shown in Fig. P4.1 (APPENDIX 4 to these ToR). |

# SECTION 2.   basic requirements for design solutions

| № | List of the data and requirements | Data and requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
| 2.1 | Requirements for the planning of land plots provided by the Customer for the placement of the LIL RW storage facility | Planning solutions for each set of the LIL RW storage facility must be developed within the boundaries established by the Customer for each of the two land plots, as shown in Figures P1.1-P1.2 (APPENDIX 1 to this ToR). |
| 2.2 | Technological requirements for buildings and structures | The design shall provide for the following: - a reinforced concrete basement for the storage cells and the delivery area for radioactive waste packages; - reinforced concrete walls for the storage cells to provide additional protection for personnel from exposure to ionizing radiation, ensuring that dose limits established by the RA radiation safety standards (5) are not exceeded; - supports for the installation of craneways and a crane; - lightweight protective structures (walls and roof) above the storage cells and delivery area to protect the radioactive waste packages, as well as the facility's systems and equipment, from precipitation and direct sunlight; - artificial lighting inside the storage cell and delivery area; - Windows in the delivery area to provide combined artificial and natural lighting; - Electric roller shutter gates for entry/exit of vehicles delivering radioactive waste packages; - A crane maintenance platform located in the delivery area; - Lightning protection for the LIL RW SF. |
| 2.3 | Other technological requirements | The design of the LIL RW storage facility must provide for using only proven technologies and equipment with proven track records of successful use at other similar facilities. Since the facility is designed for long-term storage of radioactive waste for at least 50 years, the LIL RW storage facility design must incorporate passive safety features as extensively as possible. The design shall provide for: - drainage channels for draining stormwater from adjacent areas, bypassing the LIL RW storage facilities. - stormwater drainage for the LIL RW storage facility building. |
| 2.4 | Requirements for design and space-planning solutions for structures, systems and equipment | Structural and space-planning solutions for structures and systems must comply with the requirements of regulatory and technical documentation (see Section 7) and the technical requirements given below. - SC and DA structures: The geometric dimensions of the structures, including the dimensions of the storage cell, the height and thickness of the concrete walls and the thickness of the concrete foundations, as well as the reinforcement scheme of the structures, the depth and thickness of the foundation slab shall be determined by calculations, taking into account the ensuring radiation safety outside the LIL RW storage facility and the features of the layout of the RW packages for storage, the weight and size characteristics of the RW packages (see APPENDIX 2 to this ToR) and design solutions for the use of lifting equipment, namely: - the placement of packages for storage in 16 rows, 18 pieces per row and in 4 tiers; in this case, the distance between adjacent storage positions of radioactive waste packages, in the longitudinal and transverse directions, as well as from the outermost packages of the outer rows to the enclosing structures of the storage cellss for radioactive waste packages, should not exceed 100 mm and be determined by the design of the cask's load gripper. - the movement and placement of radioactive waste packages to the positions in the storage facility, as well as the withdrawal of packages, their movement to a designated position in the delivery area for the purpose of inspection, and subsequent return to the original storage position, must be carried out using a coordinate overhead crane In this case, the thickness of the reinforced concrete walls of the SC must be at least 200 mm; the width of the DA is taken to be equal to the width of the SC of the radioactive waste packages, and the length must be at least 8 m. Provide waterproofing and protection for the surface of the reinforced concrete foundation slab, as well as measures to protect the reinforced concrete slab and walls from corrosion. Given the long service life of the storage facility, foundation slab strength calculations must be performed, taking into account creep deformation. The design must prevent cracking in the reinforced concrete slab. The storage cells of the same phase must be separated by a thermal seal. The required height of lightweight protective structures made of profiled sheet metal installed on metal supporting structures along the perimeter of the SC and DA (walls and common roof above the SC and DA) shall be determined taking into account the characteristics of the overhead crane and its maintenance platform. (See general view in Figure P3.2.) - Industrial and household unit, based on a 10 ft ISO cask The design shall provide for: - the operator's workstation for the LIL RW storage facility with a crane control panel, a control system, a radiation monitoring and control system, and auxiliary storage systems; - inverter type air conditioning system (heating and cooling). - Lifting equipment The design must include the installation of a coordinate overhead crane to perform the process of removing radioactive waste packages from the transport vehicle and transferring them from the delivery area to the radioactive waste package storage positions in the storage cells. The design must provide for the use of a single crane with a lifting capacity of 15 tons to service two modules of a single phase. The accuracy of aiming/placing radioactive waste packages at the storage positions and the associated crane characteristics must be determined taking into account the specified radioactive waste package placement layout (see paragraph 1) in the storage cell, the design features, and the weight and dimensions of the reinforced concrete structure. |
| 2.5 | Power Supply | The design shall provide for the power supply of all systems and equipment of the LIL RW SF from a power supply panel which is common for each phase, which shall be located within the boundaries of the DA. |
| 2.6 | Lighting | The design shall provide for: - artificial lighting of the SC and mixed one in the DA, - outdoor lighting around the perimeter of the LIL RW storage facilities and above the entrance/exit and vehicle entry/exit points to/from the DA. Lighting should be designed using energy-saving technologies. |
| 2.7 | Other | Intra-facility utilities are included in the design scope of the LIL RW SF. The design must provide for emergency power supply for automated fire detection systems and radiation monitoring and control systems. |
| 2.8 | Communication system | The designt must provide for a communication system compatible with the equipment of the existing communication system at the ANPP. |
| 2.9 | Video surveillance system | The design must include a video surveillance system on site. The location and number of surveillance cameras are subject to agreement with the Customer. |
| 2.10 | Fire alarm and fire extinguishing equipment | The design must provide for equipping the LIL RW SF with a fire alarm system and fire extinguishing equipment in accordance with the fire safety regulations in force in the Republic of Armenia (see SECTION 7). |
| 2.11 | Landscaping, entrances and driveways | Access roads and driveways: - roads and driveways are designed from the perimeter boundaries of the I and II phases of the LIL RW SF up to existing asphalt and concrete roads at the ANPP industrial site; The design must provide for asphalt and concrete roads with a permissible load no less than that encountered during the transportation of radioactive waste packages, taking into account the weight and dimensions of the vehicles and cargo being transported. Fencing: - The design must include fencing along the perimeter of the LIL RW SF with automatic, electrically operated sliding gates. |

# SECTION 3.   INITIAL DATA AND INFORMATION PROVIDED BY THE CUSTOMER

| № | List of data and requirements | Data and requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
| 3.1 | Technical data provided by the Customer | The Customer, at the request of the Contractor, specifies the connection points of the LIL RW SF to the existing utility networks/communications of the ANPP (electrical networks (taking into account the category of consumers), communication lines, computer network, etc.) |
| 3.2 | The number of packages of radioactive waste arriving at the facility | Up to 1,000 reinforced concrete casks containing low- and intermediate-level radioactive waste per year. The dimensional and weight characteristics of the radioactive waste packaging are contained in APPENDIX 2 to this TS. |
| 3.3 | Other initial data | Any additional data available to the ANPP that may be required for the design of the LIL RW SF, such as detailed data on waste characteristics, radiation conditions at construction sites, the master layout, and other information not included in this TS may be provided to the Contractor upon request. The Contractor is responsible for verifying and, if necessary, updating the data and information received. |

# SECTION 4.    Requirements to design documentation

| № | List of data and requirements | Data and requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
| 4.1 | Basic requirements to design documentation development | The documentation must be developed in accordance with the requirements established in the RA for the composition of design documentation sections and requirements for their content. Composition of design documentation: SECTION 1.1. Explanatory note SECTION 1.2. Initial design (sketches) for obtaining an architectural-design ToR. SECTION 1.3. Bill of quantities. SECTION 2. Land plot layout. SECTION 3. Architectural solutions. SECTION 4. Structural and space-planning solutions. SECTION 5. Information on engineering equipment, engineering and technical support networks, a list of engineering and technical measures, and the content of technological solutions. SECTION 6. Construction organization project SECTION 7. List of environmental protection measures SECTION 8. Radiation safety measures. SECTION 9. Fire safety measures SECTION 10.1 Мeasures to ensure compliance with energy efficiency requirements and requirements for equipping the buildings, structures and facilities, and equipping with the devices measuring energy resources used. SECTION 10.2 Requirements for ensuring safe operation of capital construction facilities. SECTION 11.1 Cost estimate for construction of capital construction facilities. SECTION 11.2. Consolidated cost estimate for facility construction. SECTION 12. Other documentation. |
| 4.2 | Safety assessment and development of Safety Analysis Report | The contractor is responsible for conducting the safety assessment and developing the Safety Analysis Report for the LIL RW SF. The content of the Safety Analysis Report for the LIL RW SF must comply with NP-099-17 - "Requirements for the Composition and Content of the Safety Analysis Report for Radioactive Waste Storage Facilities." |
| 4.3 | Environmental Impact Assessment (EIA) | The Contractor is responsible for developing the EIA for LIL RW SF The EIA for the LIL RW SF must include: Introduction with a brief description of the EIA objectives Description of the activity and its goals Description of alternative activity options Assessment of potential economic and environmental damage to the environment, forms and terms of compensation Assessment of individual environmental components, natural resources, and potential changes in conditions and scopes should the activity be implemented. Potential social impact Potential impact on human health Risk assessment of the consequences of potential emergencies Climate impact Justification of the compliance of the activity with approved basic documents Justification of the selected option Environmental management plan Impact monitoring program for the planned activity reference materials (maps, diagrams, graphs, tables indicating sources of initial data) Information on obstacles encountered during the assessment and report development process Potential environmental impacts during the construction, operation, and shutdown phases. |
| 4.4 | Requirements for cost-estimate documentation | Cost estimate documentation is prepared in accordance with the regulations in force in the Republic of Armenia. (see SECTION 7). |
| 4.5 | Instructions for the preparation of additional documentation as part of the project (demonstration material, its scope, form) | Demonstration materials for their presentation to the public (both hard copy (brochures) and in electronic form) are developed by the Contractor. The scope and types of demonstration materials are agreed upon separately with the Customer. |
| 4.6 | Number of copies of design documentation. | The design documentation is submitted in four (4) full copies on paper, and one (1) electronic copy in PDF format. The estimate documentation is provided in one (1) hard copy and one (1) electronic copy in Excel format. Additional formats are agreed upon at the initial design stage. |
| 4.7 | Design documentation approval | The Contractor submits design documentation for approval in Armenian (for tenders/bids, in Russian and English). The Contractor will provide the documentation and maintain it during the expert review by government authorities or licensed and/or authorized organizations and, together with the Customer, address any issues until a positive conclusion is received. Fees for the expert review by Armenian government authorities will be paid by the Armenian Nuclear Power Plant. |
| 4.8 | Other requirements | The design must comply with the regulatory documentation in effect at the time of the contract's conclusion (see SECTION 7). Subsequent changes are possible by additional agreement of the parties. |

# SECTION 5.   Additional requirements and data

| № | List of data and requirements | Data and requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
| 5.1 | Operation mode of the major equipment of the LIL RW SF | 8 hours a day, 250 days annually |
| 5.2 | Mode of operation of the personnel | In one shift, 8 hours per day |
| 5.3 | Dates of execution of works | 9 months from the date of the conclusion of the contract for the implementation of works on the LIL RW SF design. In case of delays in the execution of the contract, no later than 3 months before the expiration of the established period, the Contractor submits to the Customer a request for an extension of the period of performance of the works, with justification of the duration of the period required for the full completion of the works. The contractor's financial liability for delays is determined by the contract. |
| 5.4 | Introduction of amendments, additions | The design assignment can be clarified and supplemented by mutual agreement of the parties no later than 30 calendar days before the end of the preparation of design documentation according to the contract. |
| 5.5 | Norms and standards | SECTION 7 contains a list of general norms and standards applicable to RAO handling installations. In the case of the need to apply additional requirements, when preparing design documentation for LIL RW SF, the Contractor must prepare and agree with the ANPP upon a list of specific standards to which design solutions must comply. |
| 5.6 | Subcontractors | When engaging subcontractors, the Contractor bears full responsibility for the performance and quality of the work assigned to the subcontractor. |
| 5.7 | Designer’s supervision | The Contractor undertakes to perform the designer's supervision of the construction works, installation and commissioning of the equipment until the end of the project, including all facilities and works transferred to the subcontractor(s), according to a separate contract with the ANPP, which must be concluded at the stage of construction of the facility. |

# SECTION 6.   interfaces with the anpp systems

| № | List of the data and requirements | Data and requirements |
| --- | --- | --- |
| 1 | 2 | 3 |
| 6.1 | Interfaces with the ANPP systems | The equipment of the LIL RW SF will have interfaces with the following systems of the ANPP: - Power supply – connection to the IS 0.4 kV - Radiation monitoring and control system – transmission of information to the RSM panel - Fire water supply – connection to the fire–extinguishing network of the auxiliaries building - Fire alarm system – transmission of the alarms to the main switchboard - Communication system - connection to the plant ATS - Computer network - connection to one of the network hubs - Sediment removal system - connection to stormwater drainage system |

# SECTION 7.   NORMS ANS STANDARDS

| № | Title |
| --- | --- |
|  | INTERNATIONAL STANDARDS/DOCUMENTS/RECOMMENDATIONS |
| 1. | IAEA SF-1, Fundamental Safety Principles |
| 2. | IAEA WS-G-6.1, Storage of Radioactive Waste |
| 3. | IAEA SSR-1: Site Evaluation for Nuclear Installations |
| 4. | IAEA GSR Part 3, Radiation Protection and Safety of Radiation Sources: International Basic Safety Standards |
| 5. | IAEA Safety Standards Series No. GSR Part 4, Safety Assessment for Facilities and Activities |
| 6. | IAEA No. GSR Part 5, Predisposal Management of Radioactive Waste |
| 7. | IAEA SSR-6 rev.1, Regulations for the Safe Transport of Radioactive Material |
| 8. | IAEA GSG-1, Classification of Radioactive Waste |
| 9. | IAEA GSG-3, The Safety Case and Safety Assessment for the Predisposal Management of Radioactive Waste |
| 10. | IAEA TECDOC-1817, Selection of Technical Solutions for the Management of Radioactive Waste |
| 11. | IAEA GSR Part 6 Decommissioning of Facilities |
| 12. | Council Directive 2013/59/Euratom of 5 December 2013 laying down basic safety standards for protection against the dangers arising from exposure to ionizing radiation, and repealing Directives 89/618/Euratom, 90/641/Euratom, 96/29/Euratom, 97/43/Euratom and 2003/122/Euratom |
| 13. | WENRA Report: Waste and Spent Fuel Storage Safety Reference Levels, 2024 |
|  | NATIONAL STANDARDS/DOCUMENTS/RECOMMENDATIONS |
| 1. | HHShN 52-01, Concrete and reinforced concrete structures |
| 2. | HHShN 20.04-2020, Seismic-resistant construction design standards |
| 3. | SP 63.13330.2018, «Concrete and reinforced concrete structures» |
| 4. | SP 20.13330.2016, «Loads and Impacts» |
| 5. | SP 14.13330.2018, Construction in seismic regions |
| 6. | SP.22.13330.2011, Foundations of buildings and structures |
| 7. | NP-031-01, Standards of design of seismically resistant nuclear power plants |
| 8. | RB-011-2000, "Safety Assessment of Near-Surface Radioactive Waste Storages" |
| 9. | Law of the Republic of Armenia on the Safe Use of Atomic Energy for Peaceful Purposes NO-285 of 01.02.99. |
| 10. | RA Law on Licensing HO-193 of 30.05.01 |
| 11. | RA Law on Environmental Impact Assessment and Expertise HO-110-N dated 21.06.14 |
| 12. | Law of the Republic of Armenia on Fire Safety HO-176 of 15.05. 01 |
| 13. | RA Government Decree "On Approval of Radiation Safety Regulations" 1219-N dated 18.09.06 |
| 14. | Decree of the Government of the Republic of Armenia “On Approval of Radiation Safety Rules” 1489-N dated 18.09.06. |
| 15. | Decree of the Government of the Republic of Armenia “On Approval of the Procedure for the Radioactive Waste Management” 631-N dated 04.06.09. |
| 16. | Decree of the Government of the Republic of Armenia "On the approval of the order of licensing and the form of the license for the design of devices, equipment, systems, important for safety of facilities using atomic energy" 257-N10.02.05 |
| 17. | The procedure for issuing permits and other documents for the purpose of construction activities in the RA. Decree of the Government of the Republic of Armenia 596-N 19.03.15 |
| 18. | Order of the Chairman of the RA Committee on Urban Planning "On the approval of a number of regulatory and technical documents subject to localization and being in force on the territory of the Republic of Armenia, and recognition of the repeal of the decree of the Minister of Urban Planning of the Republic of Armenia No. 82 dated October 1, 2001" No. 11-N dated 14.06.22 |

LIST OF ABBREVIATIONS

| № | Abbreviations | Definitions |
| --- | --- | --- |
| 1. | ANPP | Armenian Nuclear Power Plant |
| 2. | АТS | Automated telephone station |
| 3. | RCC | Reinforced concrete cask |
| 4. | RLE | Review Level Earthquake |
| 5. | DA | Delivery Area |
| 6. | RSM | Radiation Safety Monitoring |
| 7. | IS | Integrated switchyard |
| 8. | RA CNSR | RA Committee for Nuclear Safety Regulation |
| 9. | SAR | Safety Analysis Report |
| 10. | SJ | Safety justification |
| 11. | EIA | Environmental Impact Assessment |
| 12. | OS | Outdoor Switchgear |
| 13. | SC | Storage Cell |
| 14. | DD | Design Documentation |
| 15. | DED | Design Estimate Documentation |
| 16. | RA | Republic of Armenia |
| 17. | RW | Radioactive waste |
| 18. | ТoR | Terms of Reference |
| 19. | TS | Technical Specification |
| 20. | LIL RW SF | Low-level and intermediate-level radwaste storage facility |
| 21. | OS | Outdoor Switchboard |
| 22. | ALARA | As Low As Reasonably Achievable |

# LIST OF APPENDICES

| Appendix number | Appendix Title | Page number |
| --- | --- | --- |
|  | Location of the components of the LIL RW SF within the industrial site of the ANPP | 15 |
|  | Weight and dimensional characteristics of radioactive waste packages and the automatic load-gripping device | 18 |
|  | Layout and general appearance of storage modules | 19 |
|  | RLE Response Spectra | 20 |

- APPENDIX 1.

LOCATION OF LIL RW SF COMPONENTS WITHIN THE ANPP INDUSTRIAL SITE

FIGURE P1.1 LAYOUT OF THE 1ST AND 2ND PHASES OF THE STORAGE FACILITY

FIGURE P.2 LAYOUT OF THE STORAGE MODULES

- APPENDIX 2.

WEIGHT AND DIMENSIONAL CHARACTERISTICS OF RADIOACTIVE WASTE PACKAGES AND AUTOMATIC LOAD-GRIPPING DEVICE

Table P2.1

| Parameter | Value |
| --- | --- |
| RAW packaging weight, kg | up to 12000 |
| External dimensions, mm |  |
| length | 1700 |
| width | 1700 |
| height | 1350 |

The weight and dimensional characteristics of the automatic load gripping device will be provided to the Customer upon a specific request.

- APPENDIX 3.

LAYOUT AND GENERAL APPEARANCE OF THE STORAGE MODULES

Figure P3.1 Layout of the storage modules and the delivery area with industrial domestic unit and a vehicle transporting radioactive waste packages for storage

Figure P3.2 General appearance of the storage modules

- APPENDIX 4

RLE FLOOR REDPONSE SPECTRA

Figure P4.1

The Contractor can offer additional interfaces not listed in this table

The dimensions of the reinforced concrete structures will be specified /confirmed by the Customer at the design stage..